## Sheet1
Velocity Pressure Method Calculation Sheet
1 | Duct Segment Identification |  |  |  |  | 1-A | 2-A | 2-A | A-B | 3-B | 3-B | B-C | B-C | ACD | FAN in | Stack
2 | Volumetric Flowrate (Q) |  |  |  | cfm | 1000 | 1000 | 1059,02 | 2059,02 | 900 | 957.98 |  | 3016698 |  | 3016698 | 3016698
3 | Minimum Transport Velocity (V) |  |  |  | fpm | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 |  | 3500 |  | 3500 | 3500
4 | Duct Diameter (D) |  |  |  | inches | 7 | 7 | 7 | 10 | 6.5 | 6.5 |  | 12 |  | 12 | 12
5 | Duct Area (A) |  |  |  | sq.ft | 0.267 | 0.267 | 0.267 | 0,545 | 0.230 | 0.230 |  | 0.785 |  | 0.785 | 0.785
6 | Actual Duct Velocity |  |  |  | fpm | 3745318 | 3745318 | 3966367 | 3778018 | 3913043 | 4170896 |  | 3842.93 |  | 3842.93 | 3842.93
7 | Duct Velocity Pressure |  |  |  | "wg | 0.875 | 0.875 | 0.980 | 0.889 | 0.955 | 1082 |  | 0.921 |  | 0.921 | 0.921
8 | HOOD SUCTION | SLOTS | Slot Area (As) |  | sq.ft
9 |  |  | Slot Velocity (Vs) |  | fpm
10 |  |  | Slot Velocity Pressure (VPs) |  | "wg
11 |  |  | Slot Loss Factor
12 |  |  | Acceleration Factor |  | 0 or 1
13 |  |  | Plenum Loss per VP | Items 11 + 12
14 |  |  | Plenum SP | Items 10 x 13 | "wg |  | 0 | 0
15 |  | Duct Entry Loss Factor |  | 0.5VP |  | 0.5 | 0.5 | 0.5
16 |  | Acceleration Factor |  |  | 0 or 1 | 1 | 1 | 1
17 |  | Duct Entry Loss per VP |  | Items 15 + 16 |  | 1.5 | 1.5 | 1.5
18 |  | Duct Entry Loss |  | Items 7x 17 | "wg | 1.313 | 1.313 | 1.47
19 |  | Other Loss |  |  | "wg | 0 | 0 | 0 | 0 |  |  |  | 0.11 | 5
20 |  | Hood Static Pressure |  | Items 14 + 18 + 19 | "wg | 1313 | 1313 | 1,47 |  | 1433 | 1623
21 | Straight Duct Length (L) |  |  |  | feet | 20 | 10 | 10 | 10 | 10 | 10 |  | 10 |  |  | 5
22 | Friction Factor (Hf) |  |  |  |  | 0.0359 | 0.0359 | 0.0358 | 0.023 | 0.039 | 0.039 |  | 0.019 |  |  | 0.019
23 | Friction Loss per VP |  |  | Items 21 x 22 |  | 0.718 | 0.359 | 0.358 | 0.23 | 0.39 | 0.39 |  | 0.19 |  |  | 0.095
24 | No. of Elbows |  |  | 90° | 60° | 1 | 0.67 | 0.67 |  | 0.67 | 0.67
25 | Elbow Loss per VP |  |  | Items 24 x Loss Factor | R/D=2 | 0.27 | 0.181 | 0.181 |  | 0.181 | 0.181
26 | No. Entries |  |  |  |  | 0 | 1 | 1 |  | 1 | 1
27 | Entry Loss per VP |  |  | Items 26 x Loss Factor |  | 0 | 0.18 | 0.18 |  | 0.18 | 0.18
28 | Special Fittings Loss Factors |  |  |  |  | 0 | 0
29 | Duct Loss per VP |  |  | Items 23 + 25 + 27 + 28 |  | 0.988 | 0.72 | 0.719 | 0.23 | 0.743 | 0.752 |  | 0.19 |  |  | 0.095
30 | Duct Loss (he) |  |  | Items 7 x 29 | "wg | 0.865 | 0.629 | 0.7046 | 0.204 | 0.709 | 0.813 |  | 0..175 |  |  | 0.087
31 | Duct SP Loss |  |  | Items 20 + 30 | "wg | 2178 | 1942 | 2174 | 2436 | 2168 | 2436 |  | 2721 |  | 7721 | 0.087
32 | Cummulative Static Pressure |  |  |  | "wg | -2178 | -1942 | -2174 | -2436 | -2168 | -2436 |  | -2721 |  | -7721 | 0.087
33 | Governing Static Pressure |  |  |  | "wg |  | -2178 | -2178 |  | -2436
34 | Corrected Volumetric Flowrate (Qcorr) |  |  |  | cfm |  | 1059,02 |  |  | 957.98
35 | Resultan Velocity Pressure (VPr) |  |  |  | "wg |  | 0.927 |  |  | 0.972
| SP FAN = SPout - Spin-VPin |  |  |  |  | TP FAN = SP FAN + VP out
| SP = |  |  |  |  | TP FAN =
| SP = "wg |  |  |  |  | TP FAN = "wg
Jawaban Soal untuk kuliah 23 Desember 2010
Velocity Pressure Method Calculation Sheet
1 | Duct Segment Identification |  |  |  |  | 1-A | 2-A | A-B | 3-B | 3-B Corr | B-C |  | C-D | FAN IN | E-F
2 | Volumetric Flowrate (Q) |  |  |  | cfm | 3363.315 | 3363.315 | 6726.63 | 1499.844 | 1546.95 | 8273.58 |  |  | 8273.58 | 8273.58
3 | Minimum Transport Velocity (V) |  |  |  | fpm | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 |  |  | 1500 | 1500
4 | Duct Diameter (D) |  |  |  | inches | 20 | 20 | 28.5 | 13.5 | 13.5 | 32 |  |  | 32 | 32
5 | Duct Area (A) |  |  |  | sq.ft | 2.18 | 2.18 | 4.428 | 0.9935 | 0.9935 | 5.582 |  |  | 5.582 | 5.582
6 | Actual Duct Velocity |  |  |  | fpm | 1542.805 | 1542.805 | 1519.11 | 1509.65 | 1557.07 | 1482.18 |  |  | 1482.18 | 1482.18
7 | Duct Velocity Pressure |  |  |  | "wg | 0.148 | 0.148 | 0.143 | 0.142 | 0.151 | 0.136 |  |  | 0.136 | 0.136
8 | HOOD SUCTION | SLOTS | Slot Area (As) |  | sq.ft | 0 | 0 | 0 | 0 | 0 | 0
9 |  |  | Slot Velocity (Vs) |  | fpm | 0 | 0 | 0 | 0 | 0 | 0
10 |  |  | Slot Velocity Pressure (VPs) |  | "wg | 0 | 0 | 0 | 0 | 0 | 0
11 |  |  | Slot Loss Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0
12 |  |  | Acceleration Factor |  | 0 or 1 | 0 | 0 | 0 | 0 | 0 | 0
13 |  |  | Plenum Loss per VP | Items 11 + 12 |  | 0 | 0 | 0 | 0 | 0 | 0
14 |  |  | Plenum SP | Items 10 x 13 | "wg | 0 | 0 | 0 | 0 | 0 | 0
15 |  | Duct Entry Loss Factor |  |  | VP | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0
16 |  | Acceleration Factor |  |  | 0 or 1 | 1 | 1 | 0 | 1 | 1 | 0
17 |  | Duct Entry Loss per VP |  | Items 15 + 16 |  | 1.08 | 1.08 | 0 | 1.08 | 1.08 | 0
18 |  | Duct Entry Loss |  | Items 7x 17 | "wg | 0.1598 | 0.1598 | 0 | 0.153 | 0.163 | 0
19 |  | Other Loss |  |  | "wg | 0 | 0 | 0 | 0 | 0 | 0 |  | 5
20 |  | Hood Static Pressure |  | Items 14 + 18 + 19 | "wg | 0.1598 | 0.1598 | 0 | 0.153 | 0.163 | 0
21 | Straight Duct Length (L) |  |  |  | feet | 20 | 10 | 10 | 10 | 10 | 15 |  |  |  | 15
22 | Friction Factor (Hf) |  |  |  |  | 0.0097 | 0.0097 | 0.0063 | 0.0156 | 0.0155 | 0.0055 |  |  |  | 0.0055
23 | Friction Loss per VP |  |  | Items 21 x 22 |  | 0.194 | 0.097 | 0.063 | 0.156 | 0.155 | 0.0825 |  |  |  | 0.0825
24 | No. of Elbows |  |  |  |  | 1 | 0.67 | 0 | 0.67 | 0.67 | 0
25 | Elbow Loss per VP |  |  | Items 24 x Loss Factor |  | 0.22 | 0.1474 | 0 | 0.1474 | 0.1474 | 0
26 | No. Entries |  |  |  | 0.18 | 0 | 1 | 0 | 1 | 1 | 0
27 | Entry Loss per VP |  |  | Items 26 x Loss Factor |  | 0 | 0.18 | 0 | 0.18 | 0.18 | 0
28 | Special Fittings Loss Factors |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
29 | Duct Loss per VP |  |  | Items 23 + 25 + 27 + 28 |  | 0.414 | 0.4244 | 0.063 | 0.4834 | 0.4824 | 0.0825 |  |  |  | 0.0825
30 | Duct Loss (he) |  |  | Items 7 x 29 | "wg | 0.061 | 0.0628 | 0.009 | 0.068 | 0.072 | 0.01122 |  |  |  | 0.01122
31 | Duct SP Loss |  |  | Items 20 + 30 | "wg | 0.2208 | 0.2226 | 0.009 | 0.221 | 0.235 | 0.01122 |  | 5.2591 |  | 0.01122
32 | Cummulative Static Pressure |  |  |  | "wg | -0.2208 | -0.2226 | -0.2351 | -0.221 | -0.2351 | 0.25907 |  | -5.2591 | -5.2591 | 0.01122
33 | Governing Static Pressure |  |  |  | "wg |  | 0.2261 |  |  | 0.24785 | -0.25907
34 | Corrected Volumetric Flowrate (Qcorr) |  |  |  | cfm |  |  |  | 1546.95
35 | Resultan Velocity Pressure (VPr) |  |  |  | "wg |  | 0.1483 |  |  | 0.145
| SP FAN = SPout - Spin-VPin |  |  |  |  | TP FAN = SP FAN + VP out
| SP = |  |  |  |  | TP FAN =
| SP = "wg |  |  |  |  | TP FAN = "wg

## Sheet2
Velocity Pressure Method Calculation Sheet
1 | Duct Segment Identification |  |  |  |  | 1-A | 2-A | A-B | 3-B | 3-B Corr | B-C | C-D | FAN IN | E-F
2 | Volumetric Flowrate (Q) |  |  |  | cfm | 3363.315 | 3363.315 | 6726.63 | 1499.844 | 1546.95 | 8273.58 |  | 8273.58 | 8273.58
3 | Minimum Transport Velocity (V) |  |  |  | fpm | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 |  | 1500 | 1500
4 | Duct Diameter (D) |  |  |  | inches | 20 | 20 | 28.5 | 13.5 | 13.5 | 32 |  | 32 | 32
5 | Duct Area (A) |  |  |  | sq.ft | 2.18 | 2.18 | 4.428 | 0.9935 | 0.9935 | 5.582 |  | 5.582 | 5.582
6 | Actual Duct Velocity |  |  |  | fpm | 1542.805 | 1542.805 | 1519.11 | 1509.65 | 1557.07 | 1482.18 |  | 1482.18 | 1482.18
7 | Duct Velocity Pressure |  |  |  | "wg | 0.148 | 0.148 | 0.143 | 0.142 | 0.151 | 0.136 |  | 0.136 | 0.136
8 | HOOD SUCTION | SLOTS | Slot Area (As) |  | sq.ft | 0 | 0 | 0 | 0 | 0 | 0
9 |  |  | Slot Velocity (Vs) |  | fpm | 0 | 0 | 0 | 0 | 0 | 0
10 |  |  | Slot Velocity Pressure (VPs) |  | "wg | 0 | 0 | 0 | 0 | 0 | 0
11 |  |  | Slot Loss Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0
12 |  |  | Acceleration Factor |  | 0 or 1 | 0 | 0 | 0 | 0 | 0 | 0
13 |  |  | Plenum Loss per VP | Items 11 + 12 |  | 0 | 0 | 0 | 0 | 0 | 0
14 |  |  | Plenum SP | Items 10 x 13 | "wg | 0 | 0 | 0 | 0 | 0 | 0
15 |  | Duct Entry Loss Factor |  |  | VP | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0
16 |  | Acceleration Factor |  |  | 0 or 1 | 1 | 1 | 0 | 1 | 1 | 0
17 |  | Duct Entry Loss per VP |  | Items 15 + 16 |  | 1.08 | 1.08 | 0 | 1.08 | 1.08 | 0
18 |  | Duct Entry Loss |  | Items 7x 17 | "wg | 0.1598 | 0.1598 | 0 | 0.153 | 0.163 | 0
19 |  | Other Loss |  |  | "wg | 0 | 0 | 0 | 0 | 0 | 0 | 5
20 |  | Hood Static Pressure |  | Items 14 + 18 + 19 | "wg | 0.1598 | 0.1598 | 0 | 0.153 | 0.163 | 0
21 | Straight Duct Length (L) |  |  |  | feet | 20 | 10 | 10 | 10 | 10 | 15 |  |  | 15
22 | Friction Factor (Hf) |  |  |  |  | 0.0097 | 0.0097 | 0.0063 | 0.0156 | 0.0155 | 0.0055 |  |  | 0.0055
23 | Friction Loss per VP |  |  | Items 21 x 22 |  | 0.194 | 0.097 | 0.063 | 0.156 | 0.155 | 0.0825 |  |  | 0.0825
24 | No. of Elbows |  |  |  |  | 1 | 0.67 | 0 | 0.67 | 0.67 | 0
25 | Elbow Loss per VP |  |  | Items 24 x Loss Factor |  | 0.22 | 0.1474 | 0 | 0.1474 | 0.1474 | 0
26 | No. Entries |  |  |  | 0.18 | 0 | 1 | 0 | 1 | 1 | 0
27 | Entry Loss per VP |  |  | Items 26 x Loss Factor |  | 0 | 0.18 | 0 | 0.18 | 0.18 | 0
28 | Special Fittings Loss Factors |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
29 | Duct Loss per VP |  |  | Items 23 + 25 + 27 + 28 |  | 0.414 | 0.4244 | 0.063 | 0.4834 | 0.4824 | 0.0825 |  |  | 0.0825
30 | Duct Loss (he) |  |  | Items 7 x 29 | "wg | 0.061 | 0.0628 | 0.009 | 0.068 | 0.072 | 0.01122 |  |  | 0.01122
31 | Duct SP Loss |  |  | Items 20 + 30 | "wg | 0.2208 | 0.2226 | 0.009 | 0.221 | 0.235 | 0.01122 | 5.2591 |  | 0.01122
32 | Cummulative Static Pressure |  |  |  | "wg | -0.2208 | -0.2226 | -0.2351 | -0.221 | -0.2351 | 0.25907 | -5.2591 | -5.2591 | 0.01122
33 | Governing Static Pressure |  |  |  | "wg |  | 0.2261 |  |  | 0.24785 | -0.25907
34 | Corrected Volumetric Flowrate (Qcorr) |  |  |  | cfm |  |  |  | 1546.95
35 | Resultan Velocity Pressure (VPr) |  |  |  | "wg |  | 0.1483 |  |  | 0.145
| SP FAN = SPout - Spin-VPin |  |  |  |  | TP FAN = SP FAN + VP out
| SP = |  |  |  |  | TP FAN =
| SP = "wg |  |  |  |  | TP FAN = "wg